## ASHP (72 Oceanic and ESP-r)
Air Source Heat Pump Spec Sheet for 72 Oceanic Dr. | [9 empty] | ESP-r Model of ASHP in Heating Mode
CHP236 | [10 empty] | Ratings
I believe the below values include the blower power (approx 400 W) in both the heat delivered and the electricity | [10 empty] | Cap (W) | COP
[11 empty] | 10750 | 3.3
Heating Mode
Spec Sheet |  |  |  |  | Metric Units |  |  |  |  | coef 1 | 0.76684 | 0.84639
Indoor Temp (F) | Outdoor Temp (F) | Heat Delivered (MBh or kBtu/h?) | Electricity (kW) | Current (A) | Indoor Temp (C) | Outdoor Temp (C) | Heat Spec (kW) | Electricity (kW) | COP Spec | coef 2 | 0.027487 | 0.018819
70 | 65 | 45.3 | 3.5 | 16.6 | 21.1111 | 18.3333 | 13264.3121 | 3500 | 3.7898 | coef 3 | 0.00028936 | -6.3729e-05
70 | 60 | 42.8 | 3.4 | 15.4 | 21.1111 | 15.5556 | 12532.286 | 3400 | 3.686 | coef 4 | -1.4658e-05 | -9.1659e-06
70 | 55 | 40.4 | 3.3 | 14.4 | 21.1111 | 12.7778 | 11829.541 | 3300 | 3.5847 | coef 5 | -5.653e-07 | -1.9991e-08
70 | 50 | 37.7 | 3.3 | 13.6 | 21.1111 | 10 | 11038.9529 | 3300 | 3.3451
70 | 47 | 36 | 3.2 | 13.1 | 21.1111 | 8.3333 | 10541.1751 | 3200 | 3.2941 | Amb T (degC) | ESP-r Heat (W) | ESP-r COP | ESP-r Cap Rated (W) | ESP-r COP Rated
70 | 45 | 34.9 | 3.2 | 12.9 | 21.1111 | 7.2222 | 10219.0837 | 3200 | 3.1935 | 20 | 13164.5429 | 3.6985 | 10750 | 3.3
70 | 40 | 32.4 | 3.1 | 12.1 | 21.1111 | 4.4444 | 9487.0576 | 3100 | 3.0603 | 19 | 13107.8921 | 3.6811 | 10750 | 3.3
70 | 35 | 29.9 | 3.1 | 11.5 | 21.1111 | 1.6667 | 8755.0316 | 3100 | 2.8242 | 18 | 13013.1617 | 3.6595 | 10750 | 3.3
70 | 30 | 28.2 | 3.1 | 11.1 | 21.1111 | -1.1111 | 8257.2539 | 3100 | 2.6636 | 17 | 12883.9954 | 3.634 | 10750 | 3.3
70 | 25 | 26 | 3 | 10.6 | 21.1111 | -3.8889 | 7613.0709 | 3000 | 2.5377 | 16 | 12723.8908 | 3.6047 | 10750 | 3.3
70 | 20 | 23.9 | 3 | 10.1 | 21.1111 | -6.6667 | 6998.1691 | 3000 | 2.3327 | 15 | 12536.2 | 3.5719 | 10750 | 3.3
70 | 17 | 22.6 | 2.9 | 9.8 | 21.1111 | -8.3333 | 6617.5155 | 2900 | 2.2819 | 14 | 12324.1289 | 3.5358 | 10750 | 3.3
70 | 15 | 21.8 | 2.9 | 9.7 | 21.1111 | -9.4444 | 6383.2672 | 2900 | 2.2011 | 13 | 12090.7378 | 3.4966 | 10750 | 3.3
70 | 10 | 19.5 | 2.8 | 9.2 | 21.1111 | -12.2222 | 5709.8032 | 2800 | 2.0392 | 12 | 11838.941 | 3.4544 | 10750 | 3.3
70 | 5 | 17.3 | 2.8 | 8.6 | 21.1111 | -15 | 5065.6203 | 2800 | 1.8092 | 11 | 11571.5071 | 3.4096 | 10750 | 3.3
70 | 0 | 15.1 | 2.7 | 8.2 | 21.1111 | -17.7778 | 4421.4374 | 2700 | 1.6376 | 10 | 11291.0587 | 3.3622 | 10750 | 3.3
70 | -5 | 12.9 | 2.6 | 7.6 | 21.1111 | -20.5556 | 3777.2544 | 2600 | 1.4528 | 9 | 11000.0726 | 3.3125 | 10750 | 3.3
70 | -10 | 10.6 | 2.6 | 6.8 | 21.1111 | -23.3333 | 3103.7905 | 2600 | 1.1938 | 8.5 | 10851.3621 | 3.2869 | 10750 | 3.3
[10 empty] | 8 | 10700.8799 | 3.2607 | 10750 | 3.3
[10 empty] | 7 | 10395.6657 | 3.207 | 10750 | 3.3
[10 empty] | 6 | 10086.4692 | 3.1515 | 10750 | 3.3
[10 empty] | 5 | 9775.184 | 3.0945 | 10750 | 3.3
[10 empty] | 4 | 9463.5575 | 3.0362 | 10750 | 3.3
[10 empty] | 3 | 9153.1916 | 2.9767 | 10750 | 3.3
[10 empty] | 2 | 8845.5422 | 2.9162 | 10750 | 3.3
[10 empty] | 1 | 8541.9192 | 2.855 | 10750 | 3.3
[10 empty] | 0 | 8243.487 | 2.7931 | 10750 | 3.3
[10 empty] | -1 | 7951.2639 | 2.7308 | 10750 | 3.3
[10 empty] | -2 | 7666.1223 | 2.6683 | 10750 | 3.3
[10 empty] | -3 | 7388.7891 | 2.6057 | 10750 | 3.3
[10 empty] | -4 | 7119.8449 | 2.5432 | 10750 | 3.3
[10 empty] | -5 | 6859.7249 | 2.4811 | 10750 | 3.3
[10 empty] | -6 | 6608.718 | 2.4194 | 10750 | 3.3
[10 empty] | -7 | 6366.9676 | 2.3583 | 10750 | 3.3
[10 empty] | -8 | 6134.4712 | 2.298 | 10750 | 3.3
[10 empty] | -9 | 5911.0803 | 2.2388 | 10750 | 3.3
[10 empty] | -10 | 5696.5007 | 2.1806 | 10750 | 3.3
[10 empty] | -11 | 5490.2922 | 2.1238 | 10750 | 3.3
[10 empty] | -12 | 5291.869 | 2.0685 | 10750 | 3.3
[10 empty] | -13 | 5100.4993 | 2.0148 | 10750 | 3.3
[10 empty] | -14 | 4915.3053 | 1.9629 | 10750 | 3.3
[10 empty] | -15 | 4735.2636 | 1.913 | 10750 | 3.3
[10 empty] | -16 | 4559.205 | 1.8652 | 10750 | 3.3
[10 empty] | -17 | 4385.8141 | 1.8197 | 10750 | 3.3
[10 empty] | -18 | 4213.63 | 1.7766 | 10750 | 3.3
[10 empty] | -19 | 4041.0459 | 1.7361 | 10750 | 3.3
[10 empty] | -20 | 3866.3089 | 1.6983 | 10750 | 3.3